## Tags
Device | Tag | RegisterType | Address | Format | Length | Access | StartBit | ActiveLow | ScanRate | Description

## Reference
ADAM-3600 tag input - one row per tag. Generated .xls follows adam-3600_tags_template.xls.
Address base (0 or 1) is asked every time the import file is generated.
Column | Required | Meaning
Device | yes | I/O device name = sheet name = left side of "Device:Tag". No ":"; not BoardIO/User Tag/Calc Tag.
Tag | yes | Tag name = right side of "Device:Tag". Full "Device:Tag" must be <= 26 characters.
RegisterType | yes | CS (FC01, prefix 0), IS (FC02, prefix 1), IR (FC04, prefix 3), HR (FC03, prefix 4).
Address | yes | Register number inside the area, without the prefix. Base-0 or base-1 - asked at generation. Result must be 1..9999.
Format | yes | See formats below. A width suffix (INT32, FLOAT32, BCD16) can replace the Length column.
Length | analog | Bits read from Modbus: 8, 16, 32 or 64. Discrete = 1 (may be left blank).
Access | yes | R (readWrite 1) or RW (readWrite 3). IS and IR are always R.
StartBit | discrete on HR/IR | Bit index 0..15 inside the register. Blank = 0 elsewhere.
ActiveLow | no | TRUE = signal reversed (active low). Blank = FALSE.
ScanRate | yes | Whole seconds (>= 1).
Description | no | Free text notes.
Format | conversionType | Meaning | Usual length
DISCRETE | 21 | Discrete bit (coil, input status, or one bit of a register) | 1
UINT | 21 | Unsigned integer | 8/16/32/64
INT | 22 | Signed integer | 8/16/32/64
UINT_SWAP | 1 | Unsigned integer, bytes swapped | 8/16/32/64
INT_SWAP | 2 | Signed integer, bytes swapped | 8/16/32/64
HIWORD_INT | 16 | High-word signed integer | 8/16/32/64
HIWORD_UINT | 17 | High-word unsigned integer | 8/16/32/64
FLOAT | 25 | IEEE 754 floating point | 32
RFLOAT | 26 | IEEE 754 floating point, reversed word order | 32
BCD | 35 | BCD | 8/16/32/64
DOUBLE | 61 | Double precision (plain double) | 64
DOUBLE_BE | 150 | Double precision, big-endian (IEEE) | 64
DOUBLE_LE | 151 | Double precision, little-endian | 64